A comparative analysis of the influence of geomagnetic pulsations of various frequency on the growth of GICs in power lines in the Murmansk region

Belakhovsky V.B.1, Pilipenko V.A.2, Selivanov V.N.3, Sakharov Ya.A.1

1 – Polar Geophysical Institute, Apatity

2 – Schmidt Institute of Physics of the Earth, Russian Academy of Sciences, Moscow

3 – Center for Physical and Technical Problems of Northern Energy, Federal Research Center, Kola Science Center, Russian Academy of Sciences, Apatity

belakhov@mail.ru

The paper presents a comparative analysis of the influence of geomagnetic pulsations of the Pg type and low-frequency pulsations of the Pc5-6, Pi3 type on the growth of geomagnetically induced currents (GICs) in the power transmission lines (PTL) of the Murmansk region using magnetometer data at the PGI Loparskaya observatory (LOP) and data from the Vykhodnoy substation (VKH), located near Murmansk.

Previously, the issue of the influence of Pg pulsations (giant pulsations) on the growth of GICs has not been considered in the scientific literature, since these pulsations have relatively small amplitude (within several tens of nT) and are quite rare in the data of ground-based magnetometers. Pg pulsations belong to the Pc4 frequency range and have a period of ~1.5-2.5 minutes; they represent a resonant wave structure in the magnetosphere, excited by ring current protons as a result of the development of kinetic instabilities. In ground-based data, Pg pulsations are more pronounced in the Y-component of the geomagnetic field. Due to their monochromatic nature, Pg pulsations can be used as a marker for assessing the influence of geomagnetic disturbance frequency on the growth of the GIC.

Approximately ten events were analyzed. Although Pg pulsations resulted in a larger jump in geomagnetic field variability (dB/dt) than Pc5-6/Pi3 pulsations, the GIC amplitude during Pg pulsation recording was smaller. The pulsation amplitudes were comparable (10-20 nT), while the frequencies differed by a factor of 5-8. Thus, as the frequency of geomagnetic pulsations decreased (from approximately 8 to 1.5 mHz), the GIC amplitude increased.

It is supposed that the skin effect causes low-frequency signals (Pc6 pulsations) to penetrate deeper into the Earth's lithosphere. This leads to an increase in the loop area and the creation of a greater magnetic flux, which leads to a higher induced EMF and, consequently, a higher GIC in the power transmission lines. The skin-layer thickness estimates for Pg and Pc6 pulsations demonstrate agreement between this mechanism and experimental observations. Therefore, when predicting the GIC in process lines, it is necessary to consider not only the dB/dt variability of the geomagnetic field, but also the frequency content of the signal.

The study was supported by grant No. 25-17-20038 from the Russian Science Foundation, https://rscf.ru/project/25-17-20038/, and a grant from the Ministry of Education and Science of the Murmansk Region.